## YJLV22
0.6/1kV-1 core aluminum conductor XLPE insulated steel tape armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Non-magnetic steel tape thickness | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
1X10 | 0.7 | 0.2 | 1.8 | 11.8 | 205.7175 | 3.08 | 58 | 47
1X16 | 0.7 | 0.2 | 1.8 | 12.9 | 246.9365 | 1.91 | 75 | 62
1X25 | 0.9 | 0.2 | 1.8 | 14.6 | 309.8452 | 1.2 | 100 | 78
1X35 | 0.9 | 0.2 | 1.8 | 15.2 | 351.7668 | 0.868 | 120 | 94
1X50 | 1 | 0.2 | 1.8 | 16.7 | 422.9991 | 0.641 | 145 | 110
1X70 | 1.1 | 0.2 | 1.8 | 18.5 | 522.6084 | 0.443 | 190 | 135
1X95 | 1.1 | 0.2 | 1.8 | 20.1 | 628.6045 | 0.32 | 235 | 160
1X120 | 1.2 | 0.2 | 1.8 | 21.7 | 738.4748 | 0.253 | 270 | 185
1X150 | 1.4 | 0.2 | 1.8 | 23.7 | 876.9306 | 0.206 | 310 | 205
1X185 | 1.6 | 0.2 | 1.8 | 25.7 | 1031.3153 | 0.164 | 355 | 235
1X240 | 1.7 | 0.2 | 1.8 | 28 | 1253.7033 | 0.125 | - | -
1X300 | 1.8 | 0.2 | 1.9 | 31 | 1495.4697 | 0.1 | - | -
1X400 | 2 | 0.2 | 2 | 35 | 1904.4989 | 0.0778 | - | -
0.6/1kV-2 core aluminum conductor XLPE insulated steel tape armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Non-magnetic steel tape thickness | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
2X2.5 | 0.7 | 0.2 | 1.8 | 13.4 | 236.4981 | 12.1 | - | 23
2X4 | 0.7 | 0.2 | 1.8 | 14.3 | 268.7245 | 7.41 | - | 30
2X6 | 0.7 | 0.2 | 1.8 | 15.3 | 307.2945 | 4.61 | - | 38
2X10 | 0.7 | 0.2 | 1.8 | 17.8 | 396.5706 | 3.08 | 50 | 47
2X16 | 0.7 | 0.2 | 1.8 | 20 | 492.6214 | 1.91 | 64 | 62
2X25 | 0.9 | 0.2 | 1.8 | 23.3 | 643.1392 | 1.2 | 86 | 78
2X35 | 0.9 | 0.2 | 1.8 | 24.6 | 738.0166 | 0.868 | 105 | 94
2X50 | 1 | 0.2 | 1.8 | 27.2 | 895.5028 | 0.641 | 125 | 110
2X70 | 1.1 | 0.2 | 1.9 | 31.4 | 1163.8952 | 0.443 | 165 | 135
2X95 | 1.1 | 0.2 | 2 | 35.5 | 1479.726 | 0.32 | 200 | 160
2X120 | 1.2 | 0.5 | 2.2 | 40.2 | 2164.026 | 0.253 | 235 | 185
2X150 | 1.4 | 0.5 | 2.3 | 44.2 | 2571.9399 | 0.206 | 270 | 205
2X185 | 1.6 | 0.5 | 2.5 | 48.9 | 3088.9291 | 0.164 | 310 | 235
0.6/1kV-3 core aluminum conductor XLPE insulated steel tape armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Non-magnetic steel tape thickness | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
3X2.5 | 0.7 | 0.2 | 1.8 | 13.9 | 257.4868 | 12.1 | - | 23
3X4 | 0.7 | 0.2 | 1.8 | 14.8 | 295.7837 | 7.41 | - | 30
3X6 | 0.7 | 0.2 | 1.8 | 16 | 341.9605 | 4.61 | - | 38
3X10 | 0.7 | 0.2 | 1.8 | 18.6 | 446.8756 | 3.08 | 50 | 47
3X16 | 0.9 | 0.2 | 1.8 | 21 | 563.1224 | 1.91 | 64 | 62
3X25 | 0.9 | 0.2 | 1.8 | 24.6 | 744.342 | 1.2 | 86 | 78
3X35 | 0.9 | 0.2 | 1.8 | 26 | 868.5388 | 0.868 | 105 | 94
3X50 | 1 | 0.2 | 1.9 | 28.9 | 1073.6585 | 0.641 | 125 | 110
3X70 | 1.1 | 0.2 | 2 | 33.9 | 1443.3005 | 0.443 | 165 | 135
3X95 | 1.1 | 0.5 | 2.2 | 39 | 2183.4497 | 0.32 | 200 | 160
3X120 | 1.2 | 0.5 | 2.3 | 42.7 | 2593.0087 | 0.253 | 235 | 185
3X150 | 1.4 | 0.5 | 2.4 | 47.5 | 3154.8799 | 0.206 | 270 | 205
3X185 | 1.6 | 0.5 | 2.6 | 52.1 | 3742.6662 | 0.164 | 310 | 235
3X240 | 1.7 | 0.5 | 2.8 | 58.3 | 4641.4543 | 0.125 | 365 | 260
3X300 | 1.8 | 0.5 | 2.9 | 63.6 | 5507.7184 | 0.1 | 420 | 290
0.6/1kV-4 core aluminum conductor XLPE insulated steel tape armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Non-magnetic steel tape thickness | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
4X2.5 | 0.7 | 0.2 | 1.8 | 14.7 | 287.8847 | 12.1 | - | 23
4X4 | 0.7 | 0.2 | 1.8 | 15.8 | 334.0388 | 7.41 | - | 30
4X6 | 0.7 | 0.2 | 1.8 | 17 | 384.0837 | 4.61 | - | 38
4X10 | 0.7 | 0.2 | 1.8 | 20 | 508.5617 | 3.08 | 50 | 47
4X16 | 0.9 | 0.2 | 1.8 | 22.7 | 649.2056 | 1.91 | 64 | 62
4X25 | 0.9 | 0.2 | 1.8 | 26.7 | 880.0176 | 1.2 | 86 | 78
4X35 | 0.9 | 0.2 | 1.8 | 28.3 | 1039.9321 | 0.868 | 105 | 94
4X50 | 1 | 0.2 | 2.1 | 32 | 1365.2372 | 0.641 | 125 | 110
4X70 | 1.1 | 0.5 | 2.1 | 38.5 | 2138.4503 | 0.443 | 165 | 135
4X95 | 1.1 | 0.5 | 2.3 | 42.9 | 2637.5955 | 0.32 | 200 | 160
4X120 | 1.2 | 0.5 | 2.4 | 47.4 | 3201.6415 | 0.253 | 235 | 185
4X150 | 1.4 | 0.5 | 2.6 | 52.3 | 3846.6163 | 0.206 | 270 | 205
4X185 | 1.6 | 0.5 | 2.7 | 57.5 | 4584.7627 | 0.164 | 310 | 235
4X240 | 1.7 | 0.5 | 3 | 64.3 | 5708.8719 | 0.125 | 365 | 260
4X300 | 1.8 | 0.5 | 3.1 | 70.3 | 6805.4864 | 0.1 | 420 | 290
0.6/1kV-5 core aluminum conductor XLPE insulated steel tape armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Non-magnetic steel tape thickness | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
5X2.5 | 0.7 | 0.2 | 1.8 | 15.6 | 321.3889 | 12.1 | - | 23
5X4 | 0.7 | 0.2 | 1.8 | 16.8 | 376.0697 | 7.41 | - | 30
5X6 | 0.7 | 0.2 | 1.8 | 18.2 | 442.5827 | 4.61 | - | 38
5X10 | 0.7 | 0.2 | 1.8 | 21.6 | 592.2699 | 3.08 | 50 | 47
5X16 | 0.7 | 0.2 | 1.8 | 24.6 | 762.7482 | 1.91 | 64 | 62
5X25 | 0.9 | 0.2 | 1.8 | 29 | 1028.6614 | 1.2 | 86 | 78
5X35 | 0.9 | 0.2 | 1.9 | 31 | 1235.8421 | 0.868 | 105 | 94
5X50 | 1 | 0.2 | 2.1 | 35.7 | 1616.4664 | 0.641 | 125 | 110
5X70 | 1.1 | 0.5 | 2.3 | 42.4 | 2528.133 | 0.443 | 165 | 135
5X95 | 1.1 | 0.5 | 2.4 | 47.2 | 3172.4209 | 0.32 | 200 | 160
5X120 | 1.2 | 0.5 | 2.6 | 51.8 | 3801.2783 | 0.253 | 235 | 185
5X150 | 1.4 | 0.5 | 2.7 | 57.6 | 4604.3546 | 0.206 | 270 | 205
5X185 | 1.6 | 0.5 | 2.9 | 63.8 | 5574.1232 | 0.164 | 310 | 235
5X240 | 1.7 | 0.5 | 3.2 | 70.7 | 6858.6277 | 0.125 | 365 | 260
5X300 | 1.8 | 0.5 | 3.4 | 78 | 8304.8856 | 0.1 | 420 | 290
0.6/1kV-3+1core aluminum conductor XLPE insulated steel tape armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Non-magnetic steel tape thickness | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
3X4+1X2.5 | 0.7/0.7 | 0.2 | 1.8 | 15.5 | 317.9558 | 7.41/12.1 | - | 30
3X6+1X4 | 0.7/0.7 | 0.2 | 1.8 | 16.8 | 370.8117 | 4.61/7.41 | - | 38
3X10+1X6 | 0.7/0.7 | 0.2 | 1.8 | 19.3 | 477.5723 | 3.08/4.61 | 50 | 47
3X16+1X10 | 0.7/0.7 | 0.2 | 1.8 | 22.1 | 614.5949 | 1.91/3.08 | 64 | 62
3X25+1X16 | 0.9/0.7 | 0.2 | 1.8 | 25.1 | 794.4956 | 1.2/1.91 | 86 | 78
3X35+1X16 | 0.9/0.7 | 0.2 | 1.8 | 26.8 | 925.9013 | 0.868/1.91 | 105 | 94
3X50+1X25 | 1/0.9 | 0.2 | 1.9 | 30.2 | 1175.4507 | 0.641/1.2 | 125 | 110
3X70+1X35 | 1.1/0.9 | 0.2 | 2 | 35.1 | 1569.8116 | 0.443/0.868 | 165 | 135
3X95+1X50 | 1.1/1.0 | 0.5 | 2.2 | 40.4 | 2359.4046 | 0.32/0.641 | 200 | 160
3X120+1X70 | 1.2/1.1 | 0.5 | 2.3 | 45 | 2885.8225 | 0.253/0.443 | 235 | 185
3X150+1X70 | 1.4/1.1 | 0.5 | 2.5 | 49.1 | 3395.7271 | 0.206/0.443 | 270 | 205
3X185+1X95 | 1.6/1.1 | 0.5 | 2.8 | 54.3 | 4069.6303 | 0.164/0.32 | 310 | 235
3X240+1X120 | 1.7/1.2 | 0.5 | 2.8 | 59.1 | 4854.8972 | 0.125/0.253 | 365 | 260
3X300+1X150 | 1.8/1.4 | 0.5 | 3 | 66 | 6027.7024 | 0.1/0.206 | 420 | 290
0.6/1kV-4+1core aluminum conductor XLPE insulated steel tape armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Non-magnetic steel tape thickness | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
4X4+1X2.5 | 0.7/0.7 | 0.2 | 1.8 | 16.3 | 364.9935 | 7.41/12.1 | - | 30
4X6+1X4 | 0.7/0.7 | 0.2 | 1.8 | 17.7 | 429.0934 | 4.61/7.41 | - | 38
4X10+1X6 | 0.7/0.7 | 0.2 | 1.8 | 20.3 | 561.4438 | 3.08/4.61 | 50 | 47
4X16+1X10 | 0.7/0.7 | 0.2 | 1.8 | 24 | 727.8802 | 1.91/3.08 | 64 | 62
4X25+1X16 | 0.9/0.7 | 0.2 | 1.8 | 28.1 | 974.0917 | 1.2/1.91 | 86 | 78
4X35+1X16 | 0.9/0.7 | 0.2 | 1.9 | 29.6 | 1133.886 | 0.868/1.91 | 105 | 94
4X50+1X25 | 1/0.9 | 0.2 | 2 | 34 | 1504.7963 | 0.641/1.2 | 125 | 110
4X70+1X35 | 1.1/0.9 | 0.5 | 2.2 | 40.3 | 2350.952 | 0.443/0.868 | 165 | 135
4X95+1X50 | 1.1/1.0 | 0.5 | 2.3 | 44.8 | 2907.3753 | 0.32/0.641 | 200 | 160
4X120+1X70 | 1.2/1.1 | 0.5 | 2.6 | 50.2 | 3587.7489 | 0.253/0.443 | 235 | 185
4X150+1X70 | 1.4/1.1 | 0.5 | 2.8 | 54.6 | 4214.5083 | 0.206/0.443 | 270 | 205
4X185+1X95 | 1.6/1.1 | 0.5 | 2.9 | 60.5 | 5133.1501 | 0.164/0.32 | 310 | 235
4X240+1X120 | 1.7/1.2 | 0.5 | 3 | 67.1 | 6288.8765 | 0.125/0.253 | 365 | 260
4X300+1X150 | 1.8/1.4 | 0.5 | 3.2 | 73.7 | 7544.4804 | 0.1/0.206 | 420 | 290
0.6/1kV-3+2 core aluminum conductor XLPE insulated steel tape armored PVC sheathed power cable
Nominal cross sectional area | Insulation thickness | Non-magnetic steel tape thickness | Sheath thickness | Approximate outer diameter | Approx. weight | Max.D.C resistance of conductor（20℃） | Current carrying capacity
mm2 | mm | mm | mm | mm | kg/km | Ω/km | In Air(A) | In Ground(A)
3X4+2X2.5 | 0.7/0.7 | 0.2 | 1.8 | 16.6 | 354.0229 | 7.41/12.1 | - | 30
3X6+2X4 | 0.7/0.7 | 0.2 | 1.8 | 18 | 415.7545 | 4.61/7.41 | - | 38
3X10+2X6 | 0.7/0.7 | 0.2 | 1.8 | 20.9 | 531.1477 | 3.08/4.61 | 50 | 47
3X16+2X10 | 0.7/0.7 | 0.2 | 1.8 | 24 | 693.5411 | 1.91/3.08 | 64 | 62
3X25+2X16 | 0.9/0.7 | 0.2 | 1.8 | 28.1 | 920.234 | 1.2/1.91 | 86 | 78
3X35+2X16 | 0.9/0.7 | 0.2 | 1.9 | 29.6 | 1033.8794 | 0.868/1.91 | 105 | 94
3X50+2X25 | 1/0.9 | 0.2 | 2 | 34 | 1399.958 | 0.641/1.2 | 125 | 110
3X70+2X35 | 1.1/0.9 | 0.5 | 2.2 | 40.3 | 2153.3436 | 0.443/0.868 | 165 | 135
3X95+2X50 | 1.1/1.0 | 0.5 | 2.3 | 44.8 | 2658.2393 | 0.32/0.641 | 200 | 160
3X120+2X70 | 1.2/1.1 | 0.5 | 2.5 | 50.2 | 3328.9272 | 0.253/0.443 | 235 | 185
3X150+2X70 | 1.4/1.1 | 0.5 | 2.6 | 54.6 | 3790.1739 | 0.206/0.443 | 270 | 205
3X185+2X95 | 1.6/1.1 | 0.5 | 2.8 | 60.5 | 4574.5167 | 0.164/0.32 | 310 | 235
3X240+2X120 | 1.7/1.2 | 0.5 | 3 | 67.1 | 5563.857 | 0.125/0.253 | 365 | 260
3X300+2X150 | 1.8/1.4 | 0.5 | 3.2 | 73.7 | 6800.5424 | 0.1/0.206 | 420 | 290